## Inventory Fields
LIGHTING INVENTORY
| LOCAL AUTHORITY - |  | COMPLETED BY - |  | DATE last revised - |  | General note: When completing free text do not use commas, apostrophes and avoid punctuation where possible.
No | Proposed | Dead Sure Equivalent | Initial Data Capture Requirements M = Mandatory O = Optional MF = Mandatory for Future Installations (Optional Retrospectively) | DATA TYPE | DATA ENTRY | Example Entries | Commentary
| GEOGRAPHICAL DATA (STREET GAZETTEER) |  |  | Geographic
1 | Street name | Street Name | M | Geographic | Free Text | eg Whitechurch Road | Please do not use commas, apostrophes etc - avoid punctuation in free text
2 | Road number | Segment | M | Geographic | Free Text | Free Text Number | Please do not use commas, apostrophes etc - avoid punctuation in free text
3 | Location | Zone | O | Geographic | Free Text | eg In front of school building gate | Please do not use commas, apostrophes etc - avoid punctuation in free text
4 | Village, town or district | Zone | O | Geographic | Free Text | Free Text | Please do not use commas, apostrophes etc - avoid punctuation in free text
5 | Zone | Zone | O | Geographic | Free Text | Free Text | This can be used By LA to grouped streets together as opposed to grouping lights
6 | Local Authority lighting unit | Unit Owner | M | Geographic | Free Text | Free Text | This is the lighting unit that is located on the Local Authority Network.
7 | TII lighting unit | Unit Owner | M | Geographic | Yes | Yes/No | Is the lighting unit located on the Transport Infrastructure Ireland Network.
8 | Flag | Comment | O | Geographic | Free Text | Free Text | This allows entry of free text to add general comments.
| ASSET DATA |  |  | Asset
9 | Equipment number | Equipment Number | Automatically Generated | Asset | Automatically Generated | Unique equipment number | This is the unique number that is assigned to a lighting unit within a database.- Automatically generated by dead sure.
10 | Unit number | Unit Number | M | Asset | Free Text | Number on column | This is the number on the column.
11 | Unit Type | Unit Type | M | Asset | Raising and Lowering Column | Column, ESP Pole, High Mast, Sign, CCTV, Feeder Pillar etc. | This is the type of mount structure used to mounting the luminaire
12 | Unit co-ord - Easting | Easting | M | Asset | Free Text | 6 figure ref | The term easting is a geographic coordinate for a lighting unit location point - ITM (Grid survey accuracy to +/- one meter).
13 | Unit co-ord - Northing | Northing | M | Asset | Free Text | 6 figure ref | The term northing is a geographic coordinate for a lighting unit location point - ITM (Grid survey accuracy to +/- one meter).
14 | Column manufacturer | Manufacturer | MF | Asset | Lamp Construction | Stainton, SAPA, Fabrikat, CU Phosco etc. | This is the manufacturer of the column.
15 | Column manufacturer type reference | Manufacturer ID | MF | Asset | Free Text | Manufacturer unique code for the column type | This relates to the manufacturers reference number that may be visible on the body of the column.
16 | Column cross sectional shape | Cross Section | M | Asset | Conical | TUB (for tubular), OCT (for Octagon), HEX (for Hexagonal), TAP (Tapered) etc. | This relates to the cross sectional style and design shape of the column.
17 | Column height (m) | Height | M | Asset | 4m | 4m, 5m, 6m, 8m, 10m, 12m, 15m, 20m, 30m etc. | This relates to the height of the Column.
18 | Column material type | Material | M | Asset | Aluminium | Steel, Aluminium, Cast Iron, Concrete, Wood etc. | Refers to the material that the column is manufactured from.
19 | Column protective coating | Protective Coating | O | Asset | G1 | As per series 1900, please specfiy RAL colour | This refers to the protective coating that may have been applied to the column at manufacture or installation or during maintenance. If the column has been painted, the RAL colour refers to the paint colour that has been applied to the column.
20 | Column base type | Flange Base | O | Asset | Sleeve Planted | Planted, Flange Plate,Other | Planted refers to the lighting column being planted into a foundation with the foundation being used to fix the column in position. Flange plated refers to the column being fixed by a bolt and nut to a fixing plate that is in turn fixed to a foundation.
21 | Column installation date | YearOfInstallation | MF | Asset | DD / MM / YY | - | This is the recorded date that the column was installed.
22 | Bracket installation date | BracketInstallDate | MF | Asset | DD / MM / YY | - | This is the recorded date that the bracket was installed.
23 | Bracket material | Attachment Type | M | Asset | Aluminium | Steel, Aluminium, Cast Iron etc. | Refers to the material that the bracket is manufactured from.
24 | Bracket type | Bracket | M | Asset | Other | Integral, demountable etc. | Related to the bracket (arm) which supports the luminaire, the bracket arm is either integral to the column or demountable from the column.
25 | Bracket dimensions | Attachment Size | M | Asset | 1 | 0.2, 0.5, 1.0m etc. Needed to undertake retro fit designs | This is the horizontal distance from the longitudinal axis of pole to the end of bracket.
26 | Number of brackets | NumberBrackets | M | Asset | Other | Typically 1 or 2 | Refers to the number of brackets on the column.
27 | Bracket tilt (degrees) | Bracket Projection | M | Asset | Other | 0,1,2,3, 5 degree or other . Needed to undertake retro fit designs | Refers to the inclination of the projection bracket above the horizontal .
28 | Luminaire mounting height (m) | Custom Field : Luminaire Height | M | Asset | Other | 4m, 5m, 6m, 8m, 10m, 12m, 15m, 20m, 30m. | Generally as per column height but could be different if bracket provides additional height and/or lower mounting heights also used for additional luminaires (e.g. pedestrian walkways).
29 | Number of luminaires | LumunaureQty | M | Asset | 3 | 1,2,Other etc | Number of Luminaires on the column.
30 | Luminaire installation date | Custom Field : LuminaireInstallDate or use Fault History | MF | Asset | DD / MM / YY | - | This is the recorded date that the Luminaire was installed.
31 | Luminaire manufacturer | Part of the lantern model definition | MF | Asset | Orangetek | Philips, Thorn, Urbis etc. | This is the name of the Luminaire manufacturer.
32 | Luminaire model | Lantern Model | MF | Asset | Free Text | Iridium SGS 203 etc. | This is the manufacturer model name of the Luminaire.
33 | Luminaire profile | Part of the lantern model definition | MF | Asset | Other | Flat Glass, Bowl, Curved Bowl etc. | These are the transparent covers that are applied to luminaire.
34 | Luminaire distribution | Part of the lantern model definition | MF | Asset | Free Text | Lamp Type/Setting reference Code | Photometric characteristic of LED lens. (Shape of light distribution on a surface)
35 | Luminaire warranty expiry date | Part of the lantern model definition | MF | Asset | DD / MM / YY | - | This is the warranty provided by the manufacturer.
36 | Light source colour temperature | Part of the lantern model definition | MF | Asset | Warm | Warm, Neutral or Cold or N/A | The metric used to characterise the colour appearance of a light source is the correlated colour temperature. Depending on this metric a light source can be classed as warn, neutral or cold.
37 | Luminaire driver type | Part of the lantern model definition | MF | Asset | 700mA CLO | Driver code, CLO and mA rating etc. | LED Drivers are used for powering LED arrays and are the equivalent of a ballast which are used to ignite a HID lamp source.
38 | Lumen output | Part of the lantern model definition | MF | Asset | Free Text | - | Light output measured in Lumens.
39 | Light source type | Component | M | Asset | Other | LED, SON,SOX etc. | LED - Light Emitting Diode SON - High Pressure Sodium SOX - Low Pressure Sodium Other
40 | Light source wattage - actual | Component | M | Asset | Other | 100W etc. | Nominal luminaire wattage.
41 | Control gear type | Component | MF | Asset | Electromagnetic | Electronic/Magnetic | Most artificial light sources other than incandescent lamps require special control gear to start the lamp and control the current after starting. Depending on the type of lamp involved, the control gear can take the form of ballasts, igniters or transformers.
42 | Lighting control | Control type | MF | Asset | Other | PECU, Time switch, CMS | Autonomous controls, such as photo-electric control units (PECUs) and time switches are generally used to switch the lights on as darkness falls and switch them off at dawn. Central management systems (CMS) provide two-way communication between a remote server and each light point of an installation.
43 | Control location | Control Location | M | Asset | Individual PECU | Individual PECU or Group Controlled PECU. | A photocell or (PECU /Photo Electric Control Unit) is an electric switch which is triggered at a specific light level. This can be done by visual assessment from the ground.
44 | Luminaire circuit protection rating | Part of the lantern model definition | MF | Asset | Other Please Specify | BS 88 6A, 10A, 13A,16A etc. | This relates to the fuse that resides in the base of the column that protects the lantern and associated cable from excessive fault currents.
45 | Circuit ID | Supply point added as unique Inventory item so this information held in other fields | MF | Asset | Free Text | - | Particular ID that is given to the lighting circuit.
46 | Supply from | Supply point added as unique Inventory item so this information held in other fields | MF | Asset | Free Text | From Feeder Pillar to Col 1 etc. | Reference number of lighting column that is connected to the feeder pillar.
47 | Supply to | Supply point added as unique Inventory item so this information held in other fields | MF | Asset | Free Text | To Col Ref XXX etc. | Reference number of next lighting column in the circuit that is connected to this respective lighting column.
48 | Electrical supply point installation date | Supply point added as unique Inventory item so this information held in other fields | MF | Asset | DD / MM / YY | - | This is the recorded date that the electrical supply point was installed.
49 | Attachment/traffic sign size (if fitted) | To be entered on the DFT Risk Assessment tab | O | Asset | Free Text | - | Attachments to Lighting column may aid to wind loading effects. Guidance in the calculation of wind loading on columns is given in BS EN 1991:1-4:2005 Section 7.
50 | Number of approved attachments (if fitted) | To be entered on the DFT Risk Assessment tab | O | Asset | Free Text | - | No of approved attachments fixed to the column.
51 | Type of approved attachment (if fitted) | To be entered on the DFT Risk Assessment tab | O | Asset | Sign Class A | Sign Class A,B or C | As per PD 6547:2004+A1:2009 Table 3.
52 | Interface pillar body manufacturer | Supply point added as unique Inventory item so this information held in other fields | MF | Asset | Free Text | - | Interface pillar body manufacturer name and details.
53 | Interface pillar body material | Supply point added as unique Inventory item so this information held in other fields | MF | Asset | 5mm Steel | - | Interface pillar body material type .
54 | Interface pillar body protection | Supply point added as unique Inventory item so this information held in other fields | MF | Asset | Free Text | - | Earthing for Interface pillar should be in accordance with ESB National Code of Practice for Customer Interface.
55 | Interface pillar drawing number | Supply point added as unique Inventory item so this information held in other fields | MF | Asset | Free Text | - | Number that is relevant to the particular drawing.
56 | Interface box installed | Service Owner Protection Type | M | Asset | No | Yes/No | This refers to whether there is an interface box installed for electricity supply to the lighting circuit.
57 | Underground Cable Type | Always exclude from job tickets | O | Asset | Other Please Specify | Concentric or Sheathed/Armour cable | This relates to the type of undergorund cable .
58 | Number of phases of electricity supply | Phases | MF | Asset | Single Phase | - | Number of electrical supply phases used.
59 | Outgoing circuit protection | Secondary Protection Type | MF | Asset | RCBO 30mA | BS 88 20A etc. | Circuit protection associated with the outgoing supply to the lighting circuit.
60 | Passive safe column type | Support | MF | Asset | HE | HE, LE, NE etc. | European standards consider three categories of passive safety support structured columns, these column types are: High energy absorbing (HE) (Energy absorbing support structures slow the vehicle considerably and thus the risk of secondary accidents with structures, trees, pedestrians and other road users can be reduced.) Low energy absorbing (LE) (Non-energy absorbing support structures permit the vehicle to continue after the impact with a limited reduction in speed. Non-energy absorbing support structures may provide a lower primary injury risk than energy absorbing support structures) Non-energy absorbing (NE) (Non-energy absorbing support structures permit the vehicle to continue after the impact with a limited reduction in speed. Non-energy absorbing support structures may provide a lower primary injury risk than energy absorbing support structures)
61 | Passive safe occupancy level | Support | MF | Asset | 0 | 0,1,2 or 3 | Support structures with no performance requirements for passive safety are classed 0. Levels 1, 2 and 3 are levels of safety in relation to impact severity for occupants. 1 being the lowest,3 being the highest.
62 | Passive safe electrical disconnection type | Service Owner Protection Type | MF | Asset | Electronic | Electronic, Mechanical etc. | Used to electrically isolate the circuit in the event of column impact.
63 | Passive safe electrical disconnection manufacture and model | Council Protection Type | MF | Asset | Free Text | - | Passive safe electrical disconnection manufacturer name and details.
| RISK ASSESSMENT DATA |  |  | Risk
64 | Ground conditions | Ground conditions | O | Risk | Average | Good /Average /Poor | Extract from PD 6547:2009 on ground conditions, in conjunction with BS EN 40-3-1 and -3. Good: Compact, well-graded sand and gravel, hard clay, well-graded fi ne and coarse sand, decomposed granite rock and soil. Good soils drain well. Average: Compact fine sand, medium clay, compact well-drained sandy loam, loose coarse sand and gravel. Average soils drain sufficiently well that water does not stand on the surface. Poor: Soft clay, clay loam, poorly compacted sand, clays containing a large amount of silt and vegetable matter, and made-up ground. Poor soil are normally wet and have poor drainage
65 | Salting of road | Salting of road | O | Risk | No | Yes/No | Is the lighting column on a roadway that is salted.
66 | Road environment | Road environment | O | Risk | Primarily vehicular | Primarily vehicular Mixed vehicular and pedestrian Wholly pedestrian | Categories of traffic as per BS 5489-1:2013.
67 | Environment situation | Environment situation | O | Risk | E1 | - | E0,E1,E2,E3,E4,E5 describes the particular type of lighting environment as per (GN 01 :2011 Institution of Lighting Professionals)
68 | Wind exposure | Wind exposure | O | Risk | Free Text | - | Wind profile expected at the column location.
69 | Designed for fatigue | Designed for fatigue | O | Risk | No | Yes/No | Applies to any column above 9m nominal height. Please refer to BS EN 40-3-3:2003 clause 8 if column is above 9m nominal height.
70 | Traffic flow | Traffic flow | O | Risk | Free Text | - | Annual average daily traffic figures.
71 | Traffic speed | Traffic speed | O | Risk | 30 km/ph | km/ph | Speed limit of carriageway.
72 | On a bridge | On a bridge | O | Risk | Free Text | - | Additional measures would be required if positioning a column upon a bridge structure, increased wind loading and planting arrangements.
73 | Pedestrian density | Pedestrian density | O | Risk | Free Text | Free Text | Free Text Number
74 | ESB network pole | Unit Type | M | Risk | No | Yes/No | Is the Luminaire fixed to a ESB pole?.
75 | ESB safety alert pole | Unit Type | M | Risk | No | Yes/No | Is this pole recognised as a safety alert pole as per ESB's safety alert.
76 | ESB network pole Luminaire Location (over or under conductor) | Unit Type | M | Risk | Over conductor | Over conductor/Under conductor | Is the bracket installed over a conductor or under a conductor . The conductor being overhead supply conductors.
| OPERATIONAL DATA |  |  | Operational
77 | Date of last cyclic of maintenance visit | Last Cyclic main | MF | Operational | DD / MM / YY | - | -
78 | Date of last group lamp replacement | Last Cyclic main | MF | Operational | DD / MM / YY | - | -
79 | Date of last cycle of cleaning | Last Cyclic main | MF | Operational | DD / MM / YY
80 | Date of last re-application of protective coating | Last Painted | MF | Operational | DD / MM / YY | - | -
81 | Basic structural inspection and condition level | Base, Shaft and column condition assessment | MF | Operational | Free Text | An understanding of structural condition of columns should be ascertained if retro fitting with LED units | TR22 provides guidance on the management of lighting supports.
82 | Date of last structure inspection and condition level | LastStructuralInspDate | MF | Operational | DD / MM / YY | - | Condition level - suggested that it is every 100 poles - sample only TBC
83 | Structural test certificate reference number | Comments | MF | Operational | Free Text | - | -
84 | Date of Electrical Installation Test & Results | Last Electrical Insp Date | MF | Operational | DD / MM / YY | - | -
85 | Electrical Installation Test Certificate Reference Number | Test Details | MF | Operational | Free Text | The condition of electrical installation should be known if embarking with retro fitting LED for H&S purposes | -
86 | Date of Last Periodic Electrical Inspection Test & Results | Inspection Date | MF | Operational | DD / MM / YY | - | -
87 | Periodic Electrical Inspection Test Certificate Reference Number | Test Details | MF | Operational | Free Text | - | -
88 | Date of last fault including emergency faults | Fault history | MF | Operational | DD / MM / YY | - | Populated in deadsure
89 | Fault type and history including emergency faults | Fault history | MF | Operational | Free Text | - | Populated in deadsure
90 | Lighting standard | Certification Type | O | Operational | ME 3 | BS 5489-1:2013 Class ME2, 3b, S5 etc. | This is the lighting standard that the lighting scheme was lit to.
91 | Non destructive column testing type | Test Details | O | Operational | Free Text |  | This is the type of Non Destructive Test carried out on column.
92 | Non destructive column testing date | Test Details | O | Operational | DD / MM / YY |  | This is date that the Non Destructive Test was carried out.
93 | In charge | Always exclude from job tickets | O | Operational | Free Text | Yes/No | Has the scheme been taken over by the Local Authority.
94 | In charge date | Always exclude from job tickets | O | Operational | DD / MM / YY | - | This is the date that the scheme was taken over by the Local Authority
95 | Patrol Scouting/Reported by Public | Fault Category | O | Operational | Patrol Scouting | Patrol Scouting/Reported by Public | -
| ENERGY DATA |  |  | Energy
96 | Billable wattage (unmetered supplies only) | Held in Component lookup list | M | Energy | Free Text | - | Total wattage of luminaire and control gear.
97 | Maximum Import Capacity (MIC) measured in kVA | Phase Run Current | O | Energy | Free Text |  | The Maximum Import Capacity (MIC) is the maximum rate of energy use (or power – measured in kVA) to be borne by your connection as agreed between ESB Networks and you the customer. If your demand exceeds your MIC, you will be penalised by your supplier in the form of Excess Capacity Charges. Therefore it is important to ensure that your MIC is set at the correct level.
98 | UMR billable code (unmetered supplies only) | Held in Switching Regime Lookup list | (Reserved for possible future use ) | Energy | (Reserved for possible future use ) | (Reserved for possible future use ) | Code to match UMR billable wattage.
99 | Switching regime | Switching Regime | M | Energy | Free Text | 24 hour, D2D, D2M70/35 Lux, 35/18 Lux etc. | This relates to the criteria at which the light turns on and off. This criteria can be determined by lux levels or time settings and/or a combination of both.
100 | Annual burn hours on UMR | Appears in table in deadsure that records burning hours for each month for each switching regime. | M | Energy | Free Text | - | This is the total amount of hours per annum that the Luminaire is lit for. Eg 4150
101 | Electricity supply point coordinates ( Easting) : | Supply point added as unique Inventory item so this information held in other fields | O | Energy | Free Text | 6 figure ref | Coordinates of the lighting circuit supply feed point.ITM (Grid survey accuracy to +/- one meter)
102 | Electricity supply point coordinates ( Northing) : | Supply point added as unique Inventory item so this information held in other fields | O | Energy | Free Text | 6 figure ref | Coordinates of the lighting circuit supply feed point. ITM (Grid survey accuracy to +/- one meter)
103 | Metered/Unmetered | Metered | M | Energy | Unmetered | Metered/Unmetered | Is the lighting circuit supply feed metered or unmetered. Typically unmetered supplies are less than 2KVA with metered supplies being greater that 2KVA.
104 | Group Metered Point Reference No. GMPRN | GMPRN | M | Energy | Free Text | ESBN number, A unique 11 digit number assigned to a group of unmetered supplies, these unmetered supplies under the GMPRN are an individual TMPRN. | ESBN number, A unique 11 digit number assigned to a group of unmetered supplies, these unmetered supplies under the GMPRN are an individual TMPRN.
105 | Metered Point Reference No: MPRN | MPRN | M | Energy | Free text | ESBN number, A unique 11 digit number assigned to every single electricity connection metered in the country. | ESBN number, A unique 11 digit number assigned to every single electricity connection metered in the country.
106 | Technical Metered Point Reference No: TMPRN | TMPRN | M | Energy | Free Text | ESBN number, A unique 11 digit number assigned to every single electricity connection metered in the country. | ESBN number, A unique 11 digit number assigned to unmetered supplied under a general GMPRN.

## Sheet1 (hidden)
Yes | Concentric | Patrol Scouting | 0 | Planted | Magnectic | 6A | 1 | 30 km/ph
No | Armoured | Reported by Public | 1 | Flange Plate | Electronic | 10A | 2 | 50 km/ph
| Sheathed | Other | 2 | Other | Other | 13A | 3 | 60 km/ph
| Armoured/Sheathed |  | 3 |  |  | 16A | 4 | 70 km/ph
| Other |  | 5 |  |  | Other | 5 | 80 km/ph
|  |  | Other |  |  |  | 6 | 100 km/ph
[7 empty] | 7 | 120 km/ph
8
9
10
Other

## Drop down lists (hidden)
Metered | Yes | Standard Column | Stainton | TUB | 4m | Steel | Root Column Base | HE | 0 | Electronic | Aluminium | Integral | 0.2 | 1 | 0 degree | Philips | Good | Primarily vehicular | E0 | Flat Glass | Warm 2200K-2700K | LED - Light Emitting Diode | 600W | Individual PECU | Electromagnetic | PECU | Sign Class A | 24 hour | 30kph | Free Text Entry | 1 | BS 6A | Concentric | Over conductor | Reported by Public | Reserved for possible future use | A1 | DD/ MM / YY | Cast iron | Single Phase | BS 6A | ME 1 | 350mA
Unmetered | No | Bollard | SAPA | TAP | 5m | Aluminium | Flange Plate Base | LE | 1 | Mechanical | Cast Iron | Demountable | 0.5 | 2 | 5 degree | Thorn | Average | Mixed vehicular and pedestrian | E1 | Deep Bowl | Neutral 3500K | SON - High Pressure Sodium | 400w | Group Controlled PECU | Electronic | Time switch | Sign Class B | D2D | 50kph |  | 2 | BS 10A | Sheathed | Under conductor | Patrol Scouting |  | A2a |  | 3mm Steel | Three Phase | BS 10A | ME 2 | 500mA
|  | ESB Pole | Fabrikat | OCT | 6m | Cast Iron | Sleeve Planted | NE | 2 | Fuse | Steel | Other Please Specify | 1 | Other Please Specify | 10 degree | Urbis | Poor | Wholly pedestrian | E2 | Curved Bowl | Cool 4100K | SOX - Low Pressure Sodium | 250w |  | LED Driver | CMS | Sign Class C | D2M70/35 Lux | 60kph |  | 3 | BS 13A | Armoured |  | Other Please Specify |  | A2b |  | 5mm Steel |  | BS 13A | ME 3 | 700mA
|  | High Mast | CU Phosco | HEX | 8m | Concrete | Other Please Specify | N/A | 3 |  | Other Please Specify |  | 1.5 |  | 15 degree | Holophane |  |  | E3 | Other Please Specify | Other Please Specify | Metal Halide | 150w |  |  | Other Please Specify |  | 35/18 Lux | 80kph |  | 4 | BS 16A | Armoured/Sheathed |  |  |  | G1 |  | Stainless Steel |  | BS 16A | ME 4 | 350mA CLO
|  | Traffic Sign | Lamp Construction | Conical | 10m | Wood |  |  | Other Please Specify |  |  |  | Other Please Specify |  | Other Please Specify | Orangetek |  |  | E4 |  |  | Other Please Specify | 180w |  |  |  |  | Other Please Specify | 100kph |  | 5 | Other Please Specify | Other Please Specify |  |  |  | G2a |  | GRP |  | RCBO 30mA | ME 5 | 500mA CLO
|  | CCTV | Other Please Specify | Other Please Specify | 12m | Other Please Specify | [9 empty] | CU Phoco |  |  | E5 |  |  |  | 135w | [5 empty] | 120kph |  | 6 | [5 empty] | G2b |  | Other Please Specify |  | Other Please Specify | ME 6 | 700mA CLO
|  | Feeder Pillar |  |  | 15m | [10 empty] | Other Please Specify | [6 empty] | 100w | [5 empty] | Other Please Specify |  | 7 | [5 empty] | Other Please Specify |  |  |  |  | CE 0 | Other Please Specify
|  | Wall Mounted |  |  | 20m | [17 empty] | 90w | [7 empty] | 8 | [10 empty] | CE 1
|  | Raising and Lowering Column |  |  | 30m | [17 empty] | 70w | [7 empty] | 9 | [10 empty] | CE 2
|  | Other Please Specify |  |  | Other Please Specify | [17 empty] | 55w | [7 empty] | 10 | [10 empty] | CE 3
[23 empty] | Other Please Specify | [7 empty] | 11 | [10 empty] | CE 4
[31 empty] | 12 | [10 empty] | CE 5
[31 empty] | Other Please Specify | [10 empty] | S1
S2
S3
S4
S5
S6
S7
Unknown